## Slide 1: CE 3372 Water Systems Design
Lesson 004: PRESSURE PIPE HYDRAULICS

## Slide 2: Outline
Hydraulics of Closed Conduits
Pipelines and Networks
Continuity
Energy Equation

## Slide 3: Conduit Hydraulics
Hydraulics is an applied science that deals with the mechanical properties of liquids.
      fluid mechanics provides the theoretical foundation for hydraulics.
In water systems (this course) the working fluid is usually water (the root of the word hydraulics)
Hydraulics also refers to machinery that use various working fluids

## Slide 4: Water characteristics
Water moves from higher to lower energy (along the path of least resistance)
      Head is energy per unit weight of a fluid.
Gravity flow – change in elevation provides the required energy
Pressure flow – change in pressure provides the required energy Pumps are used to increase energy to move water to a higher elevation or over a barrier

## Slide 5: Water characteristics
Flow of water creates friction/resistance; hence there is loss of energy along a flow pat
Flow rate is related to cross sectional flow area and mean section velocity

## Slide 6: CONTINUNITY AT DIFFERENT SECTIONS

## Slide 7: CONTINUNITY AT A JUNCTION

## Slide 8: Energy Equation
The energy equation relates the total dynamic head at two points in a system, accounting for frictional losses and any added head from a pump.
hL =
hp =
ht =
head supplied by a pump
head recovered by a turbine
head lost to friction

## Slide 9: Energy Equation application Assumptions
Pressure is hydrostatic in both cross sections
Fluid is incompressible
Density is constant at the cross section
Flow is steady

## Slide 10: Diagram
Notes: S is suction, d is distribution side
Pressure usually cancels out because both reservoirs are at atmospheric pressure
If cross sectional area remains the same at 2 points, velocity head can be neglected
NOTE: EGL and HGL remain same distance apart
IF XS area changes, velocity head changes across the pipe
Elevation is based on datum to the point

## Slide 11: Energy Equation
1
2

## Slide 12: Hydraulic grade line
HGL is a line that represents the surface/profile of water flowing in partially full pipe
If pipe is under pressure, flowing full the HGL rises to where a free surface would exist if there were a piezometer installed in the pipeline

## Slide 13: Energy grade line
EGL is a line that represents the elevation of energy head of water flowing in a conduit
It is the sum of the elevation, pressure, and velocity head at a location
Drawn above HGL at a distance equal to the velocity head

## Slide 14: HGL/EGL

## Slide 15: example
    Analyze an ordinary bucket (diameter = 1 foot) with a ½-inch hole drilled at the base of the bucket.
    Develop an equation that estimates time-to-drain for different fill depths (with an unknown drainage coefficient)
    Compare to observed data to infer a drainage coefficient

## Slide 16: ANALYSIS

## Slide 17: ANALYSIS

## Slide 18: RESULT

## Slide 19: example
Estimate discharge between two reservoirs
      Head Loss is given as
Notes: Do analysis in class – build tool in class. Direct application of energy equation.

## Slide 20: HEAD LOSS MODELS
Head Loss Models (for losses in pipes)
        Darcy-Weisbach
          Moody Chart
            Examples
          Jain Equations
        Hazen-Williams
        Chezy-Manning
Fitting (Minor) Losses

## Slide 21: Pipeline system
1
2
Pump Curve
Head Loss Model

## Slide 22: Darcy-Weisbach loss model for pipe loss
Frictional loss proportional to
      Length, Velocity^2
Inversely proportional to
      Cross sectional area
Loss coefficient (f) depends on
      Reynolds number (fluid and flow properties)
      Roughness height (pipe material properties)

## Slide 23: Moody Chart
Moody-Stanton chart is a tool to estimate the friction factor in the DW head loss model
Used for the pipe loss component of friction

## Slide 24: Examples
Three “classical” examples using Moody Chart
  Head loss for given discharge, diameter, material
  Discharge given head loss, diameter, material
  Diameter given discharge, head loss, material

## Slide 25: Example 1
  Head loss for given discharge, diameter, material

## Slide 26: Example 1
  Head loss for given discharge, diameter, material

## Slide 27: Example 1
  Head loss for given discharge, diameter, material

## Slide 28: Example 1
  Head loss for given discharge, diameter, material

## Slide 29: Example 1
  Head loss for given discharge, diameter, material

## Slide 30: Example 2
  Discharge given head loss, diameter, material

## Slide 31: Example 2
  Discharge given head loss, diameter, material

## Slide 32: Example 3
  Diameter given discharge, head loss, material

## Slide 33: Example 3
  Diameter given discharge, head loss, material

## Slide 34: Direct (Jain) Equations
An alternative to the Moody chart are regression equations that allow direct computation of discharge, diameter, or friction factor.

## Slide 35: Jain equations
Example – Build a VBA Tool
        State the programming problem
        Known (Inputs)
        Unknown (Outputs)
        Governing Equation(s)
        Test the tool

## Slide 36: Jain equations
State the programming problem:
        Write a function that takes inputs for the Jain equation and produces an estimate of discharge
        Write an interface (spreadsheet) that accepts the inputs, calls the function, and returns the computed discharge

## Slide 37: Jain equations
Known (inputs)
Engineer will specify (known):
Diameter, D; Length of pipe, L; Roughness height, e;
Viscosity, n; Gravitational acceleration constant, g;
Slope of the EGL (hf/L)

## Slide 38: Jain equations
Unknown (outputs)
Function will compute:
Discharge, Q.

## Slide 39: Jain equations
Governing Equation(s)
The Jain Equation (above) is the governing equation; however if we do some algebra to move D^2 into the square root terms and the natural logarithm we can compact the arithmetic used in computation slightly – the result is shown (below)
(ks and e are the same critters!)

## Slide 40: Jain equations
Build and Test the tool
Going to build in Excel VBA
        Provides a way to create a function that we can re-use; will find the concept handy when we build a by-hand network simulator

## Slide 41: Jain equations
Build and Test the tool
        To program in VBA we need to activate the developer environment. (Windows)

## Slide 42: Jain equations
Build and Test the tool
        To program in VBA we need to activate the developer environment. (Windows)

## Slide 43: Jain equations
Build and Test the tool
        To program in VBA we need to activate the developer environment. (Windows)

## Slide 44: Jain equations
Build and Test the tool
        To program in VBA we need to activate the developer environment. (mac_OS)

## Slide 45: Jain equations
Build and Test the tool
        To program in VBA we need to activate the developer environment. (Mac_OS)

## Slide 46: Jain equations
Build and Test the tool
        To program in VBA we need to activate the developer environment. (Mac_OS)

## Slide 47: Jain equations
Build and Test the tool
        To program in VBA we need to activate the developer environment. (Mac_OS)

## Slide 48: Jain equations
Build and Test the tool
        Once the developer tab is available the coding of the spreadsheet is pretty similar in either architecture.
        We will then open the editor in developer
        Then choose “add module” – the module is where we can directly enter programs

## Slide 49: Jain equations
Build and Test the tool
    Here we “Insert a Module” – In my case it is called Module 1. it is local to the worksheet

## Slide 50: Jain equations
Build and Test the tool
    Next we select the module and type in the required code

## Slide 51: Jain equations
Build and Test the tool
    With code built, now need an interface – that’s a normal spreadsheet looking thing
Includes a link to a fluid properties database

## Slide 52: Jain equations
Build and Test the tool
    Now need to test the tool using known solutions:

## Slide 53: Jain equations
Link to On-Line Tool
    A similar tool (to the spreadsheet just developed) is available online at:
    http://theodores-pro.ttu.edu/mytoolbox-server/Hydraulics/QGivenHeadLoss/QGivenHeadLoss.html

## Slide 54: Hazen-Williams
Frictional loss proportional to
      Length, Velocity^(1.8)
Inversely proportional to
      Cross section area (as hydraulic radius)
Loss coefficient (Ch) depends on
      Pipe material and finish
      Turbulent flow only (Re>4000)
WATER ONLY!

## Slide 55: Hazen-Williams
HW Head Loss
Discharge Form

## Slide 56: Hazen-williams
Hazen-Williams C-factor

## Slide 57: Example using hazen-williams formula

## Slide 58: Hydraulic Radius
HW is often presented as a velocity equation using the hydraulic radius

## Slide 59: Hydraulic Radius
The hydraulic radius is the ratio of cross section flow area to wetted perimeter

## Slide 60: Hydraulic Radius
For circular pipe, full flow (no free surface)
AREA
PERIMETER
D

## Slide 61: Chezy-Manning
Frictional loss proportional to
      Length, Velocity^2
Inversely proportional to
      Cross section area (as hydraulic radius)
Loss coefficient depends on
      Material, finish

## Slide 62: Fitting (Minor) Losses
Fittings, joints, elbows, inlets, outlets cause additional head loss.
Called “minor” loss not because of magnitude, but because they occur over short distances.
Typical loss model is

## Slide 63: Fitting (Minor) Losses
The loss coefficients are tabulated for different kinds of fittings

## Slide 64: Example – fitting (minor) losses

## Slide 65: Pipeline system
1
2
Pump Curve
Head Loss Model
Exit
Inlet
Elbow
Length_1
Length_2
=Length_1 + Length_2

## Slide 66: NEXT TIME
Pumps in hydraulic systems
      Pump curves
      System curves
      Power requirements