## Slide 1
Conceptual Model Representation
Check Valve (Backflow Preventer)
To system
EPANET Representation
Static Lift
Groundwater Reservoir
Pump
GW Elevation
Node Elevation
Static Lift + Connection Length
Pump

## Slide 2
Fill Depth
Node Elevation
Minimum Depth
Maximum Depth
Initial Depth
Boost Pump
Check Valve

## Slide 3
Level
TSR_2
PIPE TSR_TRAN and Isolation Valve
Booster Pump
TSR_1
PIPE TSR_OUT and Check Valve
PIPE TSR_INPUT
RULE STOPTSR2OVERFILL
IF TANK TSR-2 LEVEL > 29.5
THEN CV TSR_TRAN STATUS IS CLOSED
RULE KEEPTSR2FILLED
IF TANK TSR-2 LEVEL < 10.0
THEN CV TSR_TRAN STATUS IS OPEN
RULE STOPTSR1OVERFILL4
IF TANK TSR-1 LEVEL > 26.5
THEN PIPE FCV_TSR SETTING IS 1600
PRIORITY 4
RULE STOPTSR1OVERFILL3
IF TANK TSR-1 LEVEL > 27.5
THEN PIPE FCV_TSR SETTING IS 800
PRIORITY 3
RULE STOPTSR1OVERFILL2
IF TANK TSR-1 LEVEL > 28.5
THEN PIPE FCV_TSR SETTING IS 450
PRIORITY 2
RULE STOPTSR1OVERFILL1
IF TANK TSR-1 LEVEL > 29.5
THEN PIPE FCV_TSR SETTING IS CLOSED
PRIORITY 1
When TSR_1 is getting empty, increase inflow; full open if tank level minimum imminent
When TSR_2 is getting full , stop inflow
When TSR_2 is getting empty, allow inflow
FROM PIPELINE
TO WATER DISTRIBUTION SYSTEM
Flow Control Valve
RULE KEEPTSR1FILLED1
IF TANK TSR-1 LEVEL < 13.5
THEN PIPE FCV_TSR SETTING IS 450
PRIORITY 1
RULE KEEPTSR1FILLED2
IF TANK TSR-1 LEVEL < 12.5
THEN PIPE FCV_TSR SETTING IS 800
PRIORITY 2
RULE KEEPTSR1FILLED3
IF TANK TSR-1 LEVEL < 11.5
THEN PIPE FCV_TSR SETTING IS 1300
PRIORITY 3
RULE KEEPTSR1FILLED4
IF TANK TSR-1 LEVEL < 10.5
THEN PIPE FCV_TSR SETTING IS 2200
PRIORITY 4
When TSR_1 is getting full , slow inflow; full close if overflow imminent

## Slide 4
Level
ISR-2
PIPE ISR_1-2
ISR-1
PIPE ISR_2-PL and Check Valve
PIPE V2ISR1
RULE KEEPISR1FULL
IF TANK ISR-1 LEVEL < 27
THEN PUMP P-24W2 STATUS IS OPEN
AND PUMP P-24W3 STATUS IS OPEN
AND PUMP P-24W1 STATUS IS OPEN
AND PUMP P-25W2 STATUS IS OPEN
AND PUMP P-25W5 STATUS IS OPEN
AND PUMP P-30W3 STATUS IS OPEN
AND PUMP P-30W4 STATUS IS OPEN
AND PUMP P-30W5 STATUS IS OPEN
AND PUMP P-25W1 STATUS IS OPEN
AND PUMP P-30W6 STATUS IS OPEN
AND PUMP P-30W2 STATUS IS OPEN
AND PUMP P-25W4 STATUS IS OPEN
AND PUMP P-25W3 STATUS IS OPEN
AND PUMP P-30W1 STATUS IS OPEN
RULE STOPISR1FILL
IF TANK ISR-1 LEVEL > 29
THEN PUMP P-24W2 STATUS IS CLOSED
AND PUMP P-24W3 STATUS IS CLOSED
AND PUMP P-24W1 STATUS IS CLOSED
AND PUMP P-25W2 STATUS IS CLOSED
AND PUMP P-25W5 STATUS IS CLOSED
AND PUMP P-30W3 STATUS IS CLOSED
AND PUMP P-30W4 STATUS IS CLOSED
AND PUMP P-30W5 STATUS IS CLOSED
AND PUMP P-25W1 STATUS IS CLOSED
AND PUMP P-30W6 STATUS IS CLOSED
AND PUMP P-30W2 STATUS IS CLOSED
AND PUMP P-25W4 STATUS IS CLOSED
AND PUMP P-25W3 STATUS IS CLOSED
AND PUMP P-30W1 STATUS IS CLOSED
Activate all pumps to keep ISR-1 from empty
Keep ISR-2 above minimum level
WELLFIELD COLLECTOR
FCV_ISR2
To PIPELINE
RULE KEEP_ISR2_NON_EMPTY1
IF TANK ISR-2 LEVEL < 25
THEN PIPE FCV-ISR2 SETTING IS 450
PRIORITY 1
RULE KEEP_ISR2_NON_EMPTY2
IF TANK ISR-2 LEVEL < 24
THEN PIPE FCV-ISR2 SETTING IS 900
PRIORITY 2
RULE KEEP_ISR2_NON_EMPTY3
IF TANK ISR-2 LEVEL < 23
THEN PIPE FCV-ISR2 SETTING IS 1500
PRIORITY 3
RULE KEEP_ISR2_NON_EMPTY4
IF TANK ISR-2 LEVEL < 22
THEN PIPE FCV-ISR2 STATUS IS OPEN
PRIORITY 4
RULE STOP_ISR2_OVERFILL
IF TANK ISR-2 LEVEL > 29
THEN PIPE FCV-ISR2 STATUS IS CLOSED
Stop all pumps to keep ISR-1 from overfill
Keep ISR-2 from overflowing