[Company name]

[Document title]

[Document subtitle]

Cleveland, Theodore [Date]

Contents

List of Figures	2

Study Area	4

Modeling Assumptions	6

EPANET Conceptualizations	6

Transmission Pipeline	7

Wellfield Model	8

Storage Tank(s) Model	10

Terminal Storage Reservoir-Based Control Rules	10

Intermediate Storage Reservoir-Based Control Rules	13

References	25

Appendix – I Loss Coefficients for Different Materials	26

Appendix II Burst Pressure Guidance for HDPE	29

List of Figures

Figure 1. Study Area Overview Map	3

Figure 2. EPANET Model Layout on top of QGIS DEM	4

Figure 3. Model Summary	6

Figure 4. Booster Station at Terminal Storage Reservoir.	6

Figure 5. Conceptual and EPANET model representations of individual wells.	7

Figure 6. EPANET Representation of 8FAHC pump performance curve	7

Figure 7. Manufacturer Supplied Pump Data	8

Figure 8 Wellfield portion of EPANET model	8

Figure 9. Storage Tank Representation	9

Figure 10. TSR operating rules (initial simulations)	10

Figure 11.  System Demand at Connection to Water Distribution System	11

Figure 12.  Portion of Status Report Listing Control Rule changes to pumps and valves.	11

Figure 13 ISR operating rules (initial simulations)	12

Figure 14.  ISR/TSR Storage Tank Elevations.	13

Figure 15. Representative Wellfield Pumping Rates.	14

Figure 16. Flow at Different Locations	14

Figure 17. Node Groups for min/max pressure plots	15

Figure 18. J36-J40 Node group pressure plot.	16

Figure 19. Minimum pressure locations.	17

Figure 20. J2-J5 Node group pressure plot	17

Figure 21. Head at Node J1 and Tank TSR_1	18

Figure 22. Low Pressure Location in System (Google Earth Pro)	19

Figure 23.  Computed Pressures (psi) - JP6 is node with lowest pressure in this simulation.	19

Figure 24. ISR Booster Station Representation	21

Figure 25. caption	22

Figure 26. caption	23

Figure 30. Hazen-Williams Friction Factor for HDPE  (from https://onlinelibrary.wiley.com/doi/pdf/10.1002/9780470168103.app1)	25

Figure 31. C Values for various materials from: "Water Distribution Systems" in Land Development Handbook, Ed. S.O. Dewberry, Dewberry Inc., McGraw-Hill	26

Figure 32. Values of C for various materials from:  (http://54.243.252.9/ce-3372-webroot/3-Readings/HydraulicsNotes/hydraulics-notes-tgc.pdf)	27

Figure 33. Burst-Pressure Guidance (and another C value) from  https://hdpe.ca/assets/data/technical-data/performance-pipe/FAQ-Municipal-water.pdf	28

Figure 34.  Tabulated HDPE Pressure ratings from https://www.jmeagle.com/sites/default/files/HDPESpecSheet4710%20.pdf	29

# Study Area

Figure XX is an annotated map of the model area.  The three main parts are shown as the Terminal Storage Portion, the Transmission Pipeline Portion, and the Wellfield Portion (Collection is used interchangeably).

Figure 1. Study Area Overview Map

The unlabeled contour interval is 100 feet. The approximate elevation of the wellfield is 2800 feet, and the terminal storage area is approximately 2600 feet.

The KML file that contained the coordinates of the wellfield components, pipeline alignment, and terminal storage were loaded into QGIS to build an EPANET network.  A 30-meter DEM was downloaded from the public STRM database. The STRM data were re-projected onto the Zone 31N UTM coordinate system (approximately Cartesian at the study scale; it will render nicely in ordinary EPANET, and the auto-length algorithm can determine pipe lengths from node locations)

A “plug-in” named “QEPANET” was used in QGIS to map nodes and tanks.  The remainder of the EPANET model is built directly in the US EPA supplied software.

Figure 2. EPANET Model Layout on top of QGIS DEM

Figure XX is a map of the EPANET representation of the study area.  As various junctions and pipeline features were built in the EPANET software the corresponding elevations were obtained either by re-importing into the QGIS and extracting the elevation or by arithmetic mean of the specific locations from nearby features.

# Modeling Assumptions

Several assumptions used in the model development and implementation are listed below:

- The raw water portion of the system is not required to be maintained at 35 psi, the stipulated value in TAC 30.1.290.D§290.45 for water in a distribution system.

- Water in the Intermediate Storage Reservoirs (ISRs) is default raw water; furthermore these are atmospheric storage tanks (at-grade vertical cylinders).

- Water in the Terminal Storage Reservoirs (TSRs) is assumed to be raw; while also atmospheric reservoirs, water exiting these reservoirs is boosted into the water distribution system (WDS).  All water downstream of the booster station is to be at or above 35 psi for the various discharges in accordance with TAC 30.1.290.D§290.45 for water in a distribution system.

- TSRs + ISRs total volume is 3.0 million gallons.  Assuming that volume is 7 days of average discharge, the average daily demand (to empty tanks over 7 days) about 350 gpm. This value (350 gpm) is used as the ADD for time-varying hydraulic simulations.

- The entire system demand was placed (in the model) at the WDS node, which is to represent the current/future water distribution system.  A pipe (in the model) named “TSR_OUT” could be adjusted to approximate the entire system loss by future model users (or the entire water distribution system could be modeled from this location-and actual pipes used).

- The control rules at the ISRs were developed to the tank receiving water from the well field nearly full.  The generic rule structure was to start pumps when the tank depth approached ¾ full (22.5 feet deep), and stop pumps when the tank is 95% full (29.5 feet deep).  The tank was further constrained to not be allowed below 15 feet deep – so the bottom ½ of the tank is always available.  Given that the tank is to serve as a sand trap as well as storage these settings preserve ½ pf the tank for its clarifier role.  The tank that feeds the pipeline was initially allowed to respond to system hydraulics.

- The TSR control rules were set such that the tanks behave in tandem, and keep water levels between 1/3 and 98% full.

- The initial pumps shut down/start-up is all pumps are on/off a more elaborate scheme is tried in subsequent simulations where the pumps are shut down from closest to the ISRs to furthest, and restarted in reverse order. – this later rule set is more complex, and may introduce model instabilities.

# EPANET Conceptualizations

EPANET conceptualizations are examined below – these represent how the physical system is approximated in the hydraulic model.  The model includes the wellfield pumping from the underlying aquifer.  These flows are collected into two storage tanks labeled ISR-1 and ISR-2, both ½-million gallon atmospheric (at grade) storage tanks.  ISR-1 serves as both a storage reservoir and a grit (sand) chamber before water is transferred to ISR-2 which feeds the 21+ mile long transmission pipeline.

## Transmission Pipeline

The transmission pipeline is modeled as an approximately 110880 (21 miles) feet long, 17.43-inch ID pipe with a Hazen-Williams Loss Coefficient of 130. Figure 3 summarizes the various major components and water volumes.

Figure 3. Model Summary

The approximate total system volume is nearly 4 million gallons, and at 2100 gpm will take a little less than a day and a half to fill.

The pipeline terminates at TSR-1 which is tandem connected to TSR-2, both 1-million gallon atmospheric (at grade) storage tanks.  TSR-2 is assumed to store treated water, so it is boosted into the existing water distribution system.  In the hydraulic model this booster station is represented by a “pump” with the characteristics in Figure 4 below.  The performance curve was obtained by trial-and-error to produce slightly greater than 35-psi at the WDS node when the demand is 2100 gpm.

Figure 4. Booster Station at Terminal Storage Reservoir.

## Wellfield Model

Individual wells in the wellfield were modeled as specified groundwater elevations on the suction side of a pump (8FAHC).  The discharge side of the pump is connected to the nearest system node (in the model) through a check-valve (backflow preventer) to only allow one-way discharge, and connection pipe that includes the riser pipe length (the static lift in the diagram in Figure 5). Figure 5 depicts the conceptual model and the equivalent EPANET representations.

Figure 5. Conceptual and EPANET model representations of individual wells.

The groundwater elevations were specified as 2330 feet in the initial simulations.  Node elevations from the CALCS[59].pdf file were used for the wellfield model.  A pump curve with manufacturer specified behavior was supplied to EPANET and the input dialog box is shown below on Figure 6

Figure 6. EPANET Representation of 8FAHC pump performance curve

Figure 7 is a screen capture of the manufacturer supplied well pump performance curve for each well.

Figure 7. Manufacturer Supplied Pump Data

Figure 8 depicts the wellfield portion of the model area with the common groundwater elevation, with all wells active.

Figure 8 Wellfield portion of EPANET model

The groundwater reservoir(s) are the magenta rectangles, pumps, check valves, and connecting pipes are shown overlaid on the project base map.  All the well pumps are modeled with a check valve to prevent computed (and real) backflows.  In general if a well is inactive, the immediately downstream check valve should show a status of Closed in EPANET.  Interestingly, check valves are not treated as separate hydraulic elements but are a pipe attribute.  Other types of valves are separate entities.

## Storage Tank(s) Model

Figure 9 is a schematic of a generic storage tank representation in the EPANET model.   The actual system has two pairs of such tankage. In the schematic the important tank features are identified; the program requires specification of minimum, initial, and maximum depth the tank diameter and the tank bottom elevation.  Non-cylindrical tanks can be modeled using a depth-volume curve.  The check valve and booster pump are not part of tank specification; nor does the computer program actually air-gap the tanks as depicted, but this is a useable conceptualization.

Figure 9. Storage Tank Representation

The two storage areas are the intermediate storage reservoirs (ISR) located immediately adjacent to (North of) the wellfield, and the terminal storage reservoirs (TSR) located at the city yard, where the raw water would be treated (disinfected) and boosted into the water distribution system.

The control rule(s) to stop and start pumps (ISR), and open or close valves (TSR) are based on tank depths at any moment.  As the tank nears its maximum depth, pumps are stopped and/or inlet valves closed; as the tank nears a minimum depth inlet pumps are started and/or inlet valves are opened.

The initial simulations used severe rules (all pumps on/off) that would be modified in actual practice for smoother transitions as controls are requested.

### Terminal Storage Reservoir-Based Control Rules

The TSR rules were developed to supply water to the WDS from TSR_2 until its level is low, then transfer from TSR_1 to maintain supply.  When TSR_1 is low, then the system draws from the pipeline, which is supplied from the ISR location governed by system hydraulics.

A simple set of Rules are implemented to open and close connections based on tank water levels.

The TSR_1 rules are:

- If level > 29.5  (tank almost full) then stop inflows from pipeline, by closing valve in pipe TSR_INPUT

- If level < 10.5 (tank is 1/3 full and probably draining) then resume pipeline inflows, by opening valve in pipe TSR_INPUT

For the initial simulations these were the only rules used to control TSR_1.

The TSR_2 rules are:

- If level > 29.5  (tank almost full) then stop inflows from pipeline, by closing valve in pipe TSR_TRAN

- If level < 10.5 (tank is 1/3 full and probably draining) then resume pipeline inflows, by opening valve in pipe TSR_TRAN

For the initial simulations these were the only control rules for TSR_2. Figure 10 is a schematic of the tandem TSR tanks and the control rules implemented.

Figure 10. TSR operating rules (initial simulations)

These rules were refined by running several simulations with different set points until a relatively long (7+ days) simulation would run without errors or warnings.  The system demand was a repeating pattern of 210 to 2100 gpm as depicted in Figure 11.

Warnings (as in footnote above) are useful and don’t imply something is wrong with the simulation

Figure 11.  System Demand at Connection to Water Distribution System

Negative pressure (even if it is a consequence of elevation and possibly correct) will create a warning.    Negative pressures could be normal for flow going over a hill – still probably want to avoid such situations, hence the warning.  Other warnings are pumps turned off/on in response to system hydraulics – in the case where a pump cannot supply sufficient head at a required flow rate the pump is shut off (this generally identifies conceptualization problems).  In other cases one can ignore the warning and proceed especially if the on/off is in response to a control rule.  The status report file lists all such warnings and also lists control changes (as well as errors and related error codes).

Figure 12.  Portion of Status Report Listing Control Rule changes to pumps and valves.

Figure 12 is an example of a portion of the status report, illustrating acknowledgement of a rule induced change and a subsequent valve setting change.  Warnings are listed in the same report and by program default the modeler has to examine the file before the program will complete a simulation.

### Intermediate Storage Reservoir-Based Control Rules

The ISR rules were stipulated to supply water to the pipeline from ISR_2 until its level is low, then transfer from ISR_1 to maintain supply.  When ISR_1 is low, then the system draws from the wellfield, which is supplied to the ISR location governed by system hydraulics.

These rules are slightly more complex because a stated goal is to keep ISR_1 close to full and use it as a sand trap (aka clarifier).  The initial set points below are simply to get the modeled system to function.

The ISR_1 rules are:

- If level > 29 (tank is 96% full) then stop inflows from wellfield, by closing stopping all pumps.

- If level < 27 (tank is 90% full and probably draining) then resume wellfield inflows, by starting all pumps.

For the initial simulations these were the only rules used to control ISR_1.

The ISR_2 rules are:

- None; ISR_2 drains/fills as prescribed by pipeline hydraulics.

Figure 13 is a schematic of the tandem ISR tanks and the control rules implemented.

Figure 13 ISR operating rules (initial simulations)

This initial simulation showed that the ISR tanks function under the simulation conditions as a tandem tank system.  The TSR tanks also function in tandem (a desired behavior).  The lowest water depth in the simulation (somewhere near hour 24 and again at hour 96) is 15.37 feet above the tank bottom.  The target minimum depth was 15 feet for ISR_1.  Figure 14 is an annotated plot of the tank water surface elevations, which also depicts the tank bottom elevations.  The upper trace is the ISR tank pair; the lower trace is the TSR tank pair.  The four traces are hard to depict as the ISR and TSR tank pairs plot nearly on top of each other (anticipated for the TSR pair)

Figure 14.  ISR/TSR Storage Tank Elevations.

The wellfield cycles on/off dictated by the demand pattern and control rules.  The wells pump roughly 46 hours, then shut off for 24 hours, and resume pumping for another 46 hours. Figure 15 shows the pump rates for some of the wells.  The time 0 behavior is truncated because the simulations were started with partially full tanks (somewhere intermediate between the set points).

Figure 16 is a graph that depicts the discharge at different locations in the entire system these locations are V2ISR1 (the input pipe to ISR_1), ISR2_PL (the input pipe from ISR_2 into the transmission pipeline), TSR_INPUT, TSR_TRAN (the transfer pipe from TSR_1 to TSR_2), and TSR_OUT (the pipe into the booster station).

The graph shows that the ISR supply input closely follows the pump cycles (it lags the pumps which is anticipated), and the behavior demonstrates that the storage is used to sustain flow and accommodate flow changes. The TSR_OUT link exactly follows the demand pattern as it should – this link is adjacent to the demand node, so there should be minimal time delay as demands change. The TSR_TRAN transfer pipe behavior is indicated by the blue curve – its behavior is the most varied in the plot, occasionally dropping to zero as TSR_2 nears full capacity, but quickly restarting as demand draws down the tank level.

Figure 15. Representative Wellfield Pumping Rates.

Figure 16. Flow at Different Locations

System pressures vary considerably based on location.  Some representative locations are shown on X.

Figure 17. Node Groups for min/max pressure plots

The indicated node groups are plotted below.  The J36-J40 group is shown on Figure 18

Figure 18. J36-J40 Node group pressure plot.

This node group contains the smallest pressure in the system at 2100 gpm, which coincides with the pumps being started in response to emptying tanks, is roughly 6 psi (about 13.5 feet of head) at the pipeline crossing of FM 2007, in the EPANET model it is at the node immediately south of the road shown below on the left panel of Figure 19.

The other low pressure node group is plotted on Figure 20. This node group has a similar low pressure at node J2 which is located near the input to the TSR tank system.  Node J1 (not plotted) has a minimum pressure of about 5 psi. (~ 11 feet of head)  It is the last node before TSR_1.  A plot of the head at J1 and TSR_1 is informative and is shown on Figure 21.  The location of the node is shown on the right panel of Figure 19.

The other node groups are unremarkable – the high pressures are less than 125 psi which should be manageable for HDPE (DR-17 with nominal pressure rating of 125 psi).  Appendix II contains excerpts of burst-pressure guidance.  If a DR-21 with nominal pressure rating of 100 psi is intended, then pressure break valves at/near junction J17 would be indicated.

Figure 19. Minimum pressure locations.

Figure 20. J2-J5 Node group pressure plot

Figure 21. Head at Node J1 and Tank TSR_1

The location of the low pressure is informative – it is a consequence of a small change in elevation (as per the alignment and DEM).  Figure 22 is a Google Earth Pro rendering of the location where low pressure occurs.  It occurs at a small rise in the vicinity of FM 2007.  Similarly at nodes J2 and J1 a small rise is apparent just before reaching the city yard.

An important consideration is the EPANET simulations have “square wave” behavior which reflects that it computes hydraulics as a sequence of steady states.  The flows cannot possibly drop from 2000 gpm to 200 gpm over the entire pipeline as depicted in these plots.

Figure 22. Low Pressure Location in System (Google Earth Pro)

Variable Demand Scenario

The model was also run with a variable demand, ranging from 300 gpm to 2100 gpm (hitting the peak only one hour per 24 hours) to understand system behavior under routine use.

Figure 23. Demand at WDS

Figure 24.  Water Elevations at ISR/TSR

This case the ISR perform as intended, staying mostly full during the simulation interval.

Figure 25. Selected Pumps

The pumping system idle time is lengthened somewhat.

Figure 26. Node group J36-J40

This node group contains the smallest pressure in the system at 2100 gpm, which coincides with the pumps being started in response to emptying tanks, is roughly 6 psi (about 13.5 feet of head) at the pipeline crossing of FM 2007, in the EPANET model it is at the node immediately south of the road shown below on the left panel of Figure 19.

Perform simulations using ordinary time variation.  Save all the files for transfer to Chad.  Save copy on FreeSWMM to use as a future example.

# Water Hammer Analysis

## Case 1. 0-second shutoff, frictionless pipe

This case assumes a sudden shutdown, the valve pressure ranges from -45 psi to 70 psi using the material properties for DR-17 HDPE.  The pressure wave travel time is on the order of 250 seconds to traverse the 21 mile pipeline, roughly 5 miles per minute.  Numerical instability appears as the oscillation at the leading edge of the pressure wave.

Figure 27. Water Hammer; 0-second shutdown; no damping

## Case 1. 3-second shutoff, smooth pipe friction factor

This case assumes a sudden shutdown, the valve pressure ranges from -2 psi to 50 psi using the material properties for DR-17 HDPE.  The pressure wave travel time is on the order of 250 seconds to traverse the 21 mile pipeline, roughly 5 miles per minute.  The friction factor used is for smooth pipes at Re of about 50,000.   As velocity is slowed the friction factor about doubles.

Figure 28. Water Hammer; 3-second shutdown; frictional damping

## Case 2. 6 -second shutoff, smooth pipe friction factor

This case assumes a linear shutdown over 30 seconds, the valve pressure ranges from -30 psi to 54 psi using the material properties for DR-17 HDPE.  The pressure wave travel time is on the order of 250 seconds to traverse the 21 mile pipeline, roughly 5 miles per minute.

Figure 29. Water Hammer; 6-second shutdown; frictional damping

## Case 3. 30-second shutoff, smooth pipe friction factor

This case assumes an instant shutdown, the valve pressure ranges from -2 psi to 49 psi using the material properties for DR-17 HDPE.  The pressure wave travel time is on the order of 250 seconds to traverse the 21 mile pipeline, roughly 5 miles per minute but is damped by friction (as expected)

Figure 30. Water Hammer; 30-second shutdown; frictional damping

## Case 4. 60 -second shutoff, smooth pipe friction factor

This case assumes a linear shutdown over 30 seconds, the valve pressure ranges from -1 psi to 41 psi using the material properties for DR-17 HDPE.  The pressure wave travel time is on the order of 250 seconds to traverse the 21 mile pipeline, roughly 5 miles per minute but is damped by friction (as expected)

Figure 31 Water Hammer; 60-second shutdown; frictional damping

# Conclusions

# References

Cleveland, T. G. (2018) “Pipeline Transients — Water Hammer” pp. 141-148 in Fluid Mechanics Computations in R: A Toolkit to Accompany CE 3305 at TTU. Department of Civil, Environmental, and Construction Engineering. http://54.243.252.9/ce-3372-webroot/3-Readings/CFMinR/CFMinR.pdf

# Appendix – I Loss Coefficients for Different Materials

Various references were consulted to determine a useful value for HDPE roughness parameter in EPANET including Figure 30, Figure 31, and Figure 32.

Figure 32. Hazen-Williams Friction Factor for HDPE 
(from https://onlinelibrary.wiley.com/doi/pdf/10.1002/9780470168103.app1)

Figure 33. C Values for various materials from: "Water Distribution Systems" in Land Development Handbook, Ed. S.O. Dewberry, Dewberry Inc., McGraw-Hill

Figure 34. Values of C for various materials from: 
(http://54.243.252.9/ce-3372-webroot/3-Readings/HydraulicsNotes/hydraulics-notes-tgc.pdf)

# Appendix II - Burst Pressure Guidance for HDPE

Figure 35. Burst-Pressure Guidance (and another C value) from
 https://hdpe.ca/assets/data/technical-data/performance-pipe/FAQ-Municipal-water.pdf

Figure 36.  Tabulated HDPE Pressure ratings from https://www.jmeagle.com/sites/default/files/HDPESpecSheet4710%20.pdf

# Appendix III – EPANET Input File

[TITLE]

[JUNCTIONS]

;ID              	Elev        	Demand      	Pattern

J1              	2604.32     	0.00000     	                	;

J2              	2604.32     	0.00000     	                	;

J3              	2620.72     	0.00000     	                	;

J4              	2607.60     	0.00000     	                	;

J5              	2604.32     	0.00000     	                	;

J6              	2587.92     	0.00000     	                	;

J7              	2591.20     	0.00000     	                	;

J8              	2587.92     	0.00000     	                	;

J9              	2578.08     	0.00000     	                	;

J10             	2581.36     	0.00000     	                	;

J11             	2574.80     	0.00000     	                	;

J12             	2578.08     	0.00000     	                	;

J13             	2578.08     	0.00000     	                	;

J14             	2568.24     	0.00000     	                	;

J15             	2568.24     	0.00000     	                	;

J16             	2574.80     	0.00000     	                	;

J17             	2561.68     	0.00000     	                	;

J18             	2610.88     	0.00000     	                	;

J19             	2614.16     	0.00000     	                	;

J20             	2624.00     	0.00000     	                	;

J21             	2630.56     	0.00000     	                	;

J22             	2656.80     	0.00000     	                	;

J23             	2656.80     	0.00000     	                	;

J24             	2653.52     	0.00000     	                	;

J25             	2666.64     	0.00000     	                	;

J26             	2666.64     	0.00000     	                	;

J27             	2656.80     	0.00000     	                	;

J28             	2660.08     	0.00000     	                	;

J29             	2683.04     	0.00000     	                	;

J30             	2679.76     	0.00000     	                	;

J31             	2699.44     	0.00000     	                	;

J32             	2696.16     	0.00000     	                	;

J33             	2735.52     	0.00000     	                	;

J34             	2732.24     	0.00000     	                	;

J35             	2758.48     	0.00000     	                	;

J36             	2761.76     	0.00000     	                	;

J37             	2765.04     	0.00000     	                	;

J38             	2761.76     	0.00000     	                	;

J39             	2765.04     	0.00000     	                	;

J40             	2771.60     	0.00000     	                	;

J41             	2784.72     	0.00000     	                	;

J42             	2788.00     	0.00000     	                	;

J43             	2781.44     	0.00000     	                	;

J44             	2781.44     	0.00000     	                	;

J45             	2781.44     	0.00000     	                	;

J46             	2781.44     	0           	                	;

J47             	2781.44     	0           	                	;

J48             	2778.16     	0           	                	;

J49             	2774.88     	0           	                	;

J50             	2774.88     	0           	                	;

J51             	2781.44     	0           	                	;

J52             	2791.28     	0           	                	;

J53             	2791.28     	0           	                	;

J54             	2774.88     	0           	                	;

J55             	2784.72     	0           	                	;

J56             	2784.72     	0           	                	;

J57             	2788        	0           	                	;

J58             	2784.72     	0           	                	;

J59             	2784.72     	0           	                	;

J60             	2781.44     	0           	                	;

J61             	2781.44     	0           	                	;

J62             	2791.28     	0           	                	;

J63             	2774.88     	0           	                	;

J64             	2791.28     	0           	                	;

J65             	2784.72     	0           	                	;

J66             	2797.84     	0           	                	;

J67             	2784.72     	0           	                	;

J68             	2791.28     	0           	                	;

J69             	2791.28     	0           	                	;

J70             	2788        	0           	                	;

J71             	2797.84     	0           	                	;

J72             	2797.84     	0           	                	;

J73             	2804.4      	0           	                	;

J74             	2801.12     	0           	                	;

J75             	2804.4      	0           	                	;

J76             	2814.24     	0           	                	;

J77             	2797.84     	0           	                	;

J78             	2810.96     	0           	                	;

J79             	2814.24     	0           	                	;

J80             	2810.96     	0           	                	;

J81             	2814.24     	0           	                	;

J82             	2824.08     	0           	                	;

J83             	2781.44     	0           	                	;

WDS-IN          	2601.00     	2100        	2               	;

BOOST_IN        	2601        	0           	                	;

1               	2604.32     	0           	                	;

TCVTSR1         	2601        	0           	                	;

[RESERVOIRS]

;ID              	Head        	Pattern

R25W3           	2330        	                	;

R25W5           	2330        	                	;

R25W2           	2330        	                	;

R24W2           	2330        	                	;

R24W3           	2330        	                	;

R24W1           	2330        	                	;

R25W1           	2330        	                	;

R30W1           	2330        	                	;

R30W4           	2330        	                	;

R30W5           	2330        	                	;

R30W6           	2330        	                	;

R30W3           	2330        	                	;

R30W2           	2330        	                	;

R25W4           	2330        	                	;

[TANKS]

;ID              	Elevation   	InitLevel   	MinLevel    	MaxLevel    	Diameter    	MinVol      	VolCurve        	Overflow

TSR-1           	2601        	15          	0.0000      	30          	92          	0.0000      	                	;Terminal Storage (Z=2601.04)

TSR-2           	2601        	15          	0.0000      	30          	92          	0.0000      	                	;Terminal Storage 2 (Z=2607.6)

ISR-1           	2791.00     	22.5        	15          	30          	52.0        	0.0000      	                	;Grade 2791

ISR-2           	2791.00     	15          	0           	30          	52          	0.0000      	                	;

[PIPES]

;ID              	Node1           	Node2           	Length      	Diameter    	Roughness   	MinorLoss   	Status

1               	J45             	J44             	103.75      	17.43       	150         	0.00        	OPEN  	;

2               	J44             	J43             	63.44       	17.43       	150         	0.00        	OPEN  	;

3               	J43             	J42             	543.04      	17.43       	150         	0.00        	OPEN  	;

4               	J42             	J41             	141.37      	17.43       	150         	0.00        	OPEN  	;

5               	J41             	J40             	12253.62    	17.43       	150         	0.00        	OPEN  	;

6               	J40             	J39             	555.50      	17.43       	150         	0.00        	OPEN  	;

7               	J39             	J38             	158.26      	17.43       	150         	0.00        	OPEN  	;

8               	J38             	J37             	1255.29     	17.43       	150         	0.00        	OPEN  	;

9               	J37             	J36             	2098.64     	17.43       	150         	0.00        	OPEN  	;

10              	J36             	J35             	180.96      	17.43       	150         	0.00        	OPEN  	;

11              	J35             	J34             	5143.43     	17.43       	130         	0.00        	OPEN  	;

12              	J34             	J33             	154.09      	17.43       	130         	0.00        	OPEN  	;

13              	J33             	J32             	5444.28     	17.43       	130         	0.00        	OPEN  	;

14              	J32             	J31             	86.43       	17.43       	130         	0.00        	OPEN  	;

15              	J31             	J30             	5079.74     	17.43       	130         	0.00        	OPEN  	;

16              	J30             	J29             	95.38       	17.43       	130         	0.00        	OPEN  	;

17              	J29             	J28             	3006.91     	17.43       	130         	0.00        	OPEN  	;

18              	J28             	J27             	235.90      	17.43       	130         	0.00        	OPEN  	;

19              	J27             	J26             	2175.36     	17.43       	130         	0.00        	OPEN  	;

20              	J26             	J25             	172.13      	17.43       	130         	0.00        	OPEN  	;

21              	J25             	J24             	4964.61     	17.43       	130         	0.00        	OPEN  	;

22              	J24             	J23             	154.06      	17.43       	130         	0.00        	OPEN  	;

23              	J23             	J22             	204.70      	17.43       	130         	0.00        	OPEN  	;

24              	J22             	J21             	3800.44     	17.43       	130         	0.00        	OPEN  	;

25              	J21             	J20             	3851.41     	17.43       	130         	0.00        	OPEN  	;

26              	J20             	J19             	3178.39     	17.43       	130         	0.00        	OPEN  	;

27              	J19             	J18             	190.21      	17.43       	130         	0.00        	OPEN  	;

28              	J18             	J17             	15888.45    	17.43       	130         	0.00        	OPEN  	;

29              	J17             	J16             	1243.64     	17.43       	130         	0.00        	OPEN  	;

30              	J16             	J15             	984.75      	17.43       	130         	0.00        	OPEN  	;

31              	J15             	J14             	11142.98    	17.43       	130         	0.00        	OPEN  	;

32              	J14             	J13             	1028.97     	17.43       	130         	0.00        	OPEN  	;

33              	J13             	J12             	1006.01     	17.43       	130         	0.00        	OPEN  	;

34              	J12             	J11             	12584.41    	17.43       	130         	0.00        	OPEN  	;

35              	J11             	J10             	110.04      	17.43       	130         	0.00        	OPEN  	;

36              	J10             	J9              	822.89      	17.43       	130         	0.00        	OPEN  	;

37              	J9              	J8              	1643.15     	17.43       	130         	0.00        	OPEN  	;

38              	J8              	J7              	2617.41     	17.43       	130         	0.00        	OPEN  	;

39              	J7              	J6              	96.86       	17.43       	130         	0.00        	OPEN  	;

40              	J6              	J5              	2621.34     	17.43       	130         	0.00        	OPEN  	;

41              	J5              	J4              	933.52      	17.43       	130         	0.00        	OPEN  	;

42              	J4              	J3              	4425.24     	17.43       	130         	0.00        	OPEN  	;

43              	J3              	J2              	245.25      	17.43       	130         	0.00        	OPEN  	;

44              	J2              	J1              	2258.84     	18.00       	135.0000    	0.00        	OPEN  	;

82              	J67             	J65             	1938.8408   	6           	150         	0           	CV    	;

83              	J65             	J64             	624.5776    	12          	150         	0           	CV    	;

84              	J64             	J62             	1602.3456   	6           	150         	0           	CV    	;

85              	J62             	J61             	359.9144    	8           	150         	0           	CV    	;

86              	J61             	J60             	34.5056     	12          	150         	0           	Open  	;

87              	J60             	J59             	6.8552      	12          	150         	0           	Open  	;

88              	J59             	J58             	9.4136      	12          	150         	0           	Open  	;

89              	J58             	J56             	2110.2208   	12          	150         	0           	CV    	;

90              	J56             	J55             	10.2664     	12          	150         	0           	Open  	;

91              	J55             	J53             	1402.036    	12          	150         	0           	CV    	;

92              	J53             	J52             	348.992     	12          	150         	0           	Open  	;

93              	J52             	J51             	795.8264    	12          	150         	0           	CV    	;

94              	J51             	J50             	949.7568    	14          	150         	0           	Open  	;

95              	J82             	J81             	2047.1136   	6           	150         	0           	CV    	;

96              	J81             	J80             	14.7272     	12          	150         	0           	Open  	;

97              	J80             	J78             	19.2864     	12          	150         	0           	Open  	;

98              	J79             	J78             	28.8312     	6           	150         	0           	Open  	;

99              	J78             	J76             	936.9976    	6           	150         	0           	CV    	;

100             	J76             	J74             	770.7672    	6           	150         	0           	CV    	;

101             	J74             	J72             	1367.7928   	8           	150         	0           	CV    	;

102             	J72             	J71             	696.18      	8           	150         	0           	CV    	;

103             	J71             	J69             	2981.2576   	8           	150         	0           	CV    	;

104             	J69             	J61             	716.1552    	12          	150         	0           	CV    	;

105             	J77             	J76             	2322.8632   	12          	150         	0           	CV    	;

106             	J73             	J72             	2085.5552   	6           	150         	0           	CV    	;

107             	J66             	J65             	1302.1928   	6           	150         	0           	CV    	;

108             	J68             	J64             	1108.4432   	6           	150         	0           	CV    	;

109             	J63             	J62             	1094.4048   	6           	150         	0           	CV    	;

110             	J83             	J52             	951.9872    	12          	150         	0           	CV    	;

111             	J54             	J53             	1159.2832   	12          	150         	0           	CV    	;

112             	J57             	J56             	92.824      	12          	150         	0           	Open  	;

113             	J70             	J71             	27.6504     	12          	150         	0           	Open  	;

45              	J75             	J74             	25.68       	12          	150         	0           	Open  	;

52              	J50             	J49             	13.67       	14          	150         	0           	Open  	;

53              	J49             	J48             	16.695      	14          	150         	0           	Open  	;

54              	J48             	J47             	114.70      	14          	150         	0           	Open  	;

V2ISR1          	J47             	ISR-1           	27.24       	14          	150         	0           	CV    	;

ISR2_PL         	ISR-2           	J46             	20.172      	17.43       	150         	0           	CV    	;

56              	J46             	J45             	22.96       	17.43       	150         	0           	Open  	;

ISR_1_2         	ISR-1           	ISR-2           	87.32       	17.43       	150         	0           	CV    	;

TSR_OUT         	TSR-2           	BOOST_IN        	77.61       	17.43       	130         	0           	Open  	;Connector to Existing System

TSR_INPUT       	1               	TSR-1           	20.00       	17.43       	130         	0           	Open  	;

TSR_TRAN        	TCVTSR1         	TSR-2           	60.37       	17.43       	130         	0           	Open  	;

FCV_TSR         	J1              	1               	1000        	18          	100         	0           	Open  	;

48              	TSR-1           	TCVTSR1         	10          	18          	100         	0           	CV    	;

[PUMPS]

;ID              	Node1           	Node2           	Parameters

P-24W2          	R24W2           	J54             	HEAD 8FAHC	;

P-25W2          	R25W2           	J63             	HEAD 8FAHC	;

P-25W5          	R25W5           	J66             	HEAD 8FAHC	;

P-25W3          	R25W3           	J67             	HEAD 8FAHC	;

P-25W4          	R25W4           	J68             	HEAD 8FAHC	;

P-30W2          	R30W2           	J73             	HEAD 8FAHC	;

P-30W3          	R30W3           	J75             	HEAD 8FAHC	;

P-30W6          	R30W6           	J82             	HEAD 8FAHC	;

P-30W5          	R30W5           	J78             	HEAD 8FAHC	;

P-30W4          	R30W4           	J77             	HEAD 8FAHC	;

P-30W1          	R30W1           	J70             	HEAD 8FAHC	;

P-25W1          	R25W1           	J69             	HEAD 8FAHC	;

P-24W1          	R24W1           	J57             	HEAD 8FAHC	;

P-24W3          	R24W3           	J83             	HEAD 8FAHC	;

49              	BOOST_IN        	WDS-IN          	HEAD BOOST_TSR	SPEED 1.0	;

[VALVES]

;ID              	Node1           	Node2           	Diameter    	Type	Setting     	MinorLoss

[TAGS]

[DEMANDS]

;Junction        	Demand      	Pattern         	Category

[STATUS]

;ID              	Status/Setting

P-24W2          	Closed

P-25W2          	Closed

P-25W5          	Closed

P-25W3          	Closed

P-25W4          	Closed

P-30W2          	Closed

P-30W3          	Closed

P-30W6          	Closed

P-30W5          	Closed

P-30W4          	Closed

P-30W1          	Closed

P-25W1          	Closed

P-24W1          	Closed

P-24W3          	Closed

[PATTERNS]

;ID              	Multipliers

;12-hour step demand changes

2               	0.1         	0.1         	0.1         	0.1         	0.1         	0.1

2               	1.0         	1.0         	1.0         	1.0         	1.0         	1.0

2               	1.0         	1.0         	1.0         	1.0         	1.0         	1.0

2               	1.0         	0.1         	0.1         	0.1         	0.1         	0.1

;Constant Pattern (Same as Steady Flow Model)

1               	1           	1           	1           	1           	1           	1

1               	1           	1           	1           	1           	1           	1

1               	1           	1           	1           	1           	1           	1

1               	1           	1           	1           	1           	1           	1

;Generic Pattern Max Well Flow at Hour 0800 - Use 300 gpm as base

4               	1           	1           	2           	2.5         	3.5         	4.5

4               	6           	7           	6           	4.5         	3.5         	2.5

4               	1.5         	1           	1.5         	2.5         	3.5         	4

4               	5           	4           	3.5         	2.5         	1.5         	0.9

[CURVES]

;ID              	X-Value     	Y-Value

;PUMP: PUMP: 8FAHC 17-stage turbine lift pump (at wellhead)

8FAHC           	0           	652

8FAHC           	60          	648

8FAHC           	90          	632

8FAHC           	120         	606

8FAHC           	150         	557

8FAHC           	180         	484

8FAHC           	220         	404

;PUMP: PUMP: Booster Station TSR into WDS

BOOST_TSR       	0           	100

BOOST_TSR       	2100        	70

BOOST_TSR       	4000        	6

;PUMP: PUMP: Wellhead Booster

WB              	0           	812

WB              	112         	717

WB              	168         	485

;PUMP: PUMP: BoosterStationISRExit

BOOST_ISR       	0           	120

BOOST_ISR       	2100        	114

BOOST_ISR       	4200        	99

;PUMP: PUMP: BoosterStation-Intermediate

BOOST_JP16      	0           	55

BOOST_JP16      	2100        	52

BOOST_JP16      	4200        	42

[CONTROLS]

[RULES]

RULE KEEPISR1FULL

IF TANK ISR-1 LEVEL < 27

THEN PUMP P-24W2 STATUS IS OPEN

AND PUMP P-24W3 STATUS IS OPEN

AND PUMP P-24W1 STATUS IS OPEN

AND PUMP P-25W2 STATUS IS OPEN

AND PUMP P-25W5 STATUS IS OPEN

AND PUMP P-30W3 STATUS IS OPEN

AND PUMP P-30W4 STATUS IS OPEN

AND PUMP P-30W5 STATUS IS OPEN

AND PUMP P-25W1 STATUS IS OPEN

AND PUMP P-30W6 STATUS IS OPEN

AND PUMP P-30W2 STATUS IS OPEN

AND PUMP P-25W4 STATUS IS OPEN

AND PUMP P-25W3 STATUS IS OPEN

AND PUMP P-30W1 STATUS IS OPEN

RULE STOPISR1FILL

IF TANK ISR-1 LEVEL > 29

THEN PUMP P-24W2 STATUS IS CLOSED

AND PUMP P-24W3 STATUS IS CLOSED

AND PUMP P-24W1 STATUS IS CLOSED

AND PUMP P-25W2 STATUS IS CLOSED

AND PUMP P-25W5 STATUS IS CLOSED

AND PUMP P-30W3 STATUS IS CLOSED

AND PUMP P-30W4 STATUS IS CLOSED

AND PUMP P-30W5 STATUS IS CLOSED

AND PUMP P-25W1 STATUS IS CLOSED

AND PUMP P-30W6 STATUS IS CLOSED

AND PUMP P-30W2 STATUS IS CLOSED

AND PUMP P-25W4 STATUS IS CLOSED

AND PUMP P-25W3 STATUS IS CLOSED

AND PUMP P-30W1 STATUS IS CLOSED

RULE STOPTSR2OVERFILL

IF TANK TSR-2 LEVEL > 29.5

THEN CV TSR_TRAN STATUS IS CLOSED

RULE KEEPTSR2FILLED

IF TANK TSR-2 LEVEL < 10.0

THEN CV TSR_TRAN STATUS IS OPEN

RULE STOPTSR1OVERFILL

IF TANK TSR-1 LEVEL > 29.5

THEN PIPE TSR_INPUT STATUS IS CLOSED

RULE KEEPTSR1FILLED

IF TANK TSR-1 LEVEL < 10.5

THEN PIPE TSR_INPUT STATUS IS OPEN

[ENERGY]

Global Efficiency  	75

Global Price       	0

Demand Charge      	0

[EMITTERS]

;Junction        	Coefficient

J1              	0.00

J2              	0.00

J3              	0.00

J4              	0.00

J5              	0.00

J6              	0.00

J7              	0.00

J8              	0.00

J9              	0.00

J10             	0.00

J11             	0.00

J12             	0.00

J13             	0.00

J14             	0.00

J15             	0.00

J16             	0.00

J17             	0.00

J18             	0.00

J19             	0.00

J20             	0.00

J21             	0.00

J22             	0.00

J23             	0.00

J24             	0.00

J25             	0.00

J26             	0.00

J27             	0.00

J28             	0.00

J29             	0.00

J30             	0.00

J31             	0.00

J32             	0.00

J33             	0.00

J34             	0.00

J35             	0.00

J36             	0.00

J37             	0.00

J38             	0.00

J39             	0.00

J40             	0.00

J41             	0.00

J42             	0.00

J43             	0.00

J44             	0.00

J45             	0.00

J46             	0.00

J47             	0.00

J48             	0.00

J49             	0.00

J50             	0.00

J51             	0.00

J52             	0.00

J53             	0.00

J54             	0.00

J55             	0.00

J56             	0.00

J57             	0.00

J58             	0.00

J59             	0.00

J60             	0.00

J61             	0.00

J62             	0.00

J63             	0.00

J64             	0.00

J65             	0.00

J66             	0.00

J67             	0.00

J68             	0.00

J69             	0.00

J70             	0.00

J71             	0.00

J72             	0.00

J73             	0.00

J74             	0.00

J75             	0.00

J76             	0.00

J77             	0.00

J78             	0.00

J79             	0.00

J80             	0.00

J81             	0.00

J82             	0.00

J83             	0.00

[QUALITY]

;Node            	InitQual

[SOURCES]

;Node            	Type        	Quality     	Pattern

R30W5           	CONCEN      	1000        	1

[REACTIONS]

;Type     	Pipe/Tank       	Coefficient

[REACTIONS]

Order Bulk            	1

Order Tank            	1

Order Wall            	1

Global Bulk           	0

Global Wall           	0

Limiting Potential    	0

Roughness Correlation 	0

[MIXING]

;Tank            	Model

[TIMES]

Duration           	196:00

Hydraulic Timestep 	0:01

Quality Timestep   	0:05

Pattern Timestep   	1:00

Pattern Start      	0:00

Report Timestep    	1:00

Report Start       	0:00

Start ClockTime    	00:00

Statistic          	NONE

[REPORT]

Status             	Full

Summary            	No

Page               	0

[OPTIONS]

Units              	GPM

Headloss           	H-W

Specific Gravity   	1.0

Viscosity          	1.0

Trials             	40

Accuracy           	0.001

CHECKFREQ          	2

MAXCHECK           	10

DAMPLIMIT          	0

Unbalanced         	Continue 10

Pattern            	1

Demand Multiplier  	1.0

Emitter Exponent   	0.5

Quality            	None mg/L

Diffusivity        	1.0

Tolerance          	0.01

[COORDINATES]

;Node            	X-Coord           	Y-Coord

J1              	641814.170        	3474046.260

J2              	642174.170        	3473459.180

J3              	642174.170        	3473384.410

J4              	643500.630        	3473137.950

J5              	643553.250        	3473417.650

J6              	644341.480        	3473285.740

J7              	644342.700        	3473256.240

J8              	645140.640        	3473265.010

J9              	645633.590        	3473175.790

J10             	645803.270        	3472990.990

J11             	645830.570        	3472971.490

J12             	648271.440        	3470011.340

J13             	648441.120        	3469755.840

J14             	648563.990        	3469467.190

J15             	649669.840        	3466254.960

J16             	649794.670        	3465981.910

J17             	650020.910        	3465677.650

J18             	653391.120        	3462198.220

J19             	653410.620        	3462143.610

J20             	654065.940        	3461429.780

J21             	654081.540        	3460255.670

J22             	654916.300        	3459452.120

J23             	654916.300        	3459389.710

J24             	654951.400        	3459358.500

J25             	654970.910        	3457845.030

J26             	654931.900        	3457809.920

J27             	654943.600        	3457146.800

J28             	654959.200        	3457076.590

J29             	654970.910        	3456159.920

J30             	654993.330        	3456141.400

J31             	655012.840        	3454592.820

J32             	654996.260        	3454572.340

J33             	655013.810        	3452912.590

J34             	655048.920        	3452881.380

J35             	655060.620        	3451313.300

J36             	655021.610        	3451274.290

J37             	655033.320        	3450634.570

J38             	654842.180        	3450303.010

J39             	654853.880        	3450256.200

J40             	655002.110        	3450174.290

J41             	655061.050        	3446438.890

J42             	655033.460        	3446405.780

J43             	654867.920        	3446403.020

J44             	654854.390        	3446389.200

J45             	654856.490        	3446357.640

J46             	654856.060        	3446350.650

J47             	654834.150        	3446326.550

J48             	654799.220        	3446324.930

J49             	654794.740        	3446322.510

J50             	654792.930        	3446318.750

J51             	654800.190        	3446033.000

J52             	654748.750        	3445795.890

J53             	654726.120        	3445691.920

J54             	654380.690        	3445766.720

J55             	654635.590        	3445274.170

J56             	654635.150        	3445271.070

J57             	654663.140        	3445266.870

J58             	654539.420        	3444634.870

J59             	654538.650        	3444632.110

J60             	654537.540        	3444630.340

J61             	654530.680        	3444622.370

J62             	654459.410        	3444538.930

J63             	654205.780        	3444755.720

J64             	654142.030        	3444167.550

J65             	654018.310        	3444022.800

J66             	653716.430        	3444280.640

J67             	653634.310        	3443573.400

J68             	654399.140        	3443948.240

J69             	654697.400        	3444481.380

J70             	655604.610        	3444406.810

J71             	655602.550        	3444398.640

J72             	655804.400        	3444333.010

J73             	655608.480        	3443728.110

J74             	656201.180        	3444204.710

J75             	656204.150        	3444211.960

J76             	656416.550        	3444110.710

J77             	656700.530        	3444759.470

J78             	656678.430        	3443996.590

J79             	656685.690        	3444001.540

J80             	656683.050        	3443992.960

J81             	656684.370        	3443988.670

J82             	656637.860        	3443366.290

J83             	655032.550        	3445735.080

WDS-IN          	641822.894        	3474128.901

BOOST_IN        	641833.841        	3474121.635

1               	641812.268        	3474061.294

TCVTSR1         	641842.722        	3474060.143

R25W3           	653629.234        	3442168.042

R25W5           	652658.601        	3445169.196

R25W2           	653116.026        	3445738.188

R24W2           	653673.861        	3446385.277

R24W3           	655793.635        	3446061.733

R24W1           	655403.151        	3445381.173

R25W1           	655235.800        	3444968.375

R30W1           	655603.971        	3444934.905

R30W4           	657054.343        	3445570.837

R30W5           	657902.253        	3444008.898

R30W6           	656630.388        	3442123.415

R30W3           	656920.463        	3445916.695

R30W2           	655559.345        	3442112.258

R25W4           	654443.674        	3442156.885

TSR-1           	641832.240        	3474054.830

TSR-2           	641885.570        	3474083.130

ISR-1           	654842.390        	3446327.570

ISR-2           	654857.987        	3446348.849

[VERTICES]

;Link            	X-Coord           	Y-Coord

ISR_1_2         	654850.419        	3446328.391

ISR_1_2         	654856.065        	3446333.768

[LABELS]

;X-Coord             Y-Coord             Label & Anchor Node

654988.295        	3446320.946       	"Empty Tank Elev = 2791"

643070.753        	3474498.797       	"Empty Tank Elev = 2601"

[BACKDROP]

DIMENSIONS  	641069.852        	3441832.292       	657444.848        	3475580.259

UNITS          	None

FILE

OFFSET         	0.00            	0.00

[END]

# Appendix IV  - Water Hammer R Script

The script below is adapted from:

Cleveland, T. G. (2018) “Pipeline Transients — Water Hammer” pp. 141-148 in Fluid Mechanics Computations in R: A Toolkit to Accompany CE 3305 at TTU. Department of Civil, Environmental, and Construction Engineering. http://54.243.252.9/ce-3372-webroot/3-Readings/CFMinR/CFMinR.pdf

It is intended to be run in an ordinary R environment. It was developed for pedagogical purposes, and at best is an approximation of general characteristics of system behavior.

###################################################################################

#Pipeline Transients using Explicit Finite Differences (linearized formulation)   #

###################################################################################

rm(list=ls()) # deallocate memory

######## prototype functions ###############

celerity <- function(density,elasticity_fluid,elasticity_solid,diameter,thickness){

temp1<- 1.0/elasticity_fluid

temp2<- diameter/(elasticity_solid*thickness)

temp3<- temp1 + temp2

temp4<- density*temp3

celerity <- sqrt(1.0/temp4)

return(celerity)

}

### Simulator Code ##############################

# Simulation Conditions (this section could be replaced with an input file)

# fluid properties

density <- 1000  #kg/m^3

elasticity_fluid <- 2.0e09 #Pa (2.0 GPa)

elasticity_solid <- 1.5e09 #Pa (1.5 GPa)

diameter <-  0.4572 #m (18 inches nominal for DR17 spec)

thickness <- 0.02689 #m (1.059 inhces for DR17 spec)

cc <- celerity(density,elasticity_fluid,elasticity_solid,diameter,thickness)

message("Celerity (m/sec) : ",round(cc,3))

# simulation properties

deltax <- 845.125 #meters (60 elements)

courantRatio <- 0.9876 #select courant ratio to set time step.  If bigger than 1 unstable

deltat <- courantRatio*(deltax/cc) # force to be courant number for stability

# allocate head and velocity vectors, assign initial values

elevValve = 793 #meters

elevTank = 850.9 #meters

startHead <- 859-elevTank #total head meters above tank bottom 8.84=(2820-2791)/3.28 from EPANET at ISR_2

startVelo <- 0.92 #meters/second 3.02/3.28 from EPANET at ISR2_PL

pipeLength <- 33805 #meters 21*5280/3.28 from manual calculation

closeTime <- 0 #seconds

simulationDuration <- 1800 #seconds

frictionFactor <- 0.02 #Moody Chart smooth pipe should be OK for HDPE; Re = 50,000

cellCount <- as.integer((pipeLength/deltax)+1)

head <- numeric(0)

velocity <- numeric(0)

for(i in 1:cellCount){

head[i]<-startHead

velocity[i]<-startVelo

}

###################################################################################

# useful constants

dtdx <- deltat/deltax

cc2g <- cc^2/9.81

do2 <- 1.0/(diameter*2) #used when friction included

#### force full-open velocity to agree with startVelo #######

c_factor = sqrt(2*9.8*(head[1]))/startVelo # used to simulate valve closure over finite time.

#c_factor = 1.0

##############################################

# allocate some output vectors

etime<-numeric(0)

headvalve<-numeric(0)

velocitytank<-numeric(0)

# simulation values

etime[1] <- 0

headvalve[1] <- head[cellCount]

velocitytank[1] <-velocity[1]

######################

# Time Stepping Loop #

######################

maxiter <- 1+simulationDuration/deltat

for(itime in 2:maxiter){

etime[itime]<-etime[itime-1]+deltat

###### valve closure model ##############

closeRatio <- 1-(etime[itime]/closeTime)

if(closeRatio >= 0.0){

velocity[cellCount] <- closeRatio*sqrt(2*9.8*(head[1]))/c_factor

}

else{

velocity[cellCount] <- 0

}

####### update velocity #########

for(i in 1:(cellCount-1)){

friction <- frictionFactor*velocity[i]*abs(velocity[i])*do2

velocity[i]=velocity[i]-9.81*dtdx*(head[i+1]-head[i])-deltat*friction

}

####### update head #########

for(i in 2:(cellCount)){

head[i]=head[i]-cc2g*dtdx*(velocity[i]-velocity[i-1])

}

headvalve[itime]<-head[cellCount]

velocitytank[itime] <-velocity[1]

}

# report results

if(frictionFactor <= 0.0001){

message("Frictionless Simulation - Expect Square Wave")

} else{

message("Friction factor             : ",round(frictionFactor,3))

}

########################

message("Courant number  Dt (seconds): ",round(deltat,3))

message("Valve closure time (seconds): ",round(closeTime,3))

message("Maximum head at valve (feet): ",round(3.28*(max(headvalve)),3))

message("Max. pressure at valve (psi): ",round(14.75*(max(headvalve))/10,3))

message("Minimum head at valve (feet): ",round(3.28*(min(headvalve)),3))

message("Min. pressure at valve (psi): ",round(14.75*(min(headvalve))/10,3))

# plot results

par(mfrow=c(2,1))

plot(etime,headvalve,type="l",pch=19,lwd=3,tck=1,xlab="Time (seconds)",ylab="Head at Valve (meters)",col="red")

plot(etime,velocitytank,type="l",pch=19,lwd=3,tck=1,xlab="Time (seconds)",ylab="Velocity at Tank (meters/sec)",col="blue")

#

###########

The Shuttle Radar Topography Mission (SRTM) was flown aboard the space shuttle Endeavour February 11-22, 2000. The National Aeronautics and Space Administration (NASA) and the National Geospatial-Intelligence Agency (NGA) participated in an international project to acquire radar data which were used to create the first near-global set of land elevations.  Endeavour orbited Earth 16 times each day during the 11-day mission, completing 176 orbits. SRTM successfully collected single-pass interferometry radar data over 80% of the Earth's land surface between 60° north and 56° south latitude with data points posted every 1 arc-second (approximately 30 meters).

QEPANET does not entirely work with recent QGIS; however it does work well enough to extract spatial coordinates and elevations for “node-type” objects, so it was used herein to obtain coordinates and elevations for use in the EPANET model.

A reasonable value for new pipe of various materials, HDPE probably has a higher value of around 150, so the 130 is conservative to some extent.  A couple of references for loss coefficients are attached in Appendix I

These two tanks are located in the north portion of the maps above; on the QGIS map the northern tank icon is apparent.  The tank icon at the southern part of the model are the two ISR tanks.

Errors stop program execution and need immediate attention.  Warnings are notifications to the modeler that an unusual condition exists.

Nearly all the pipelines connecting pumps to the collection tanks have check valves – hence stopping a pump usually causes the program to close the immediate downstream check valve.  This conceptualization was employed to prevent computed backward flows.

Recall that all wells are on/off in these initial simulations.